BCX-H1020

The BCX-H1020is designed to control any type of switched load. The power circuit is of a “feed through” design and is electrically equivalent to a 6 pole contactor, with the additional advantage of each pole being separately controllable via the DyNet network.  The BCX-1020is DIN rail mountable, designed to be installed in a switchboard next to the circuit breakers feeding the circuits to be controlled

Feature

- Airborne real-time clock with automatic daylight correction and automatic leap year adjustment function.

- Multifunction inlet for connection button, switch, sensor.

- Independent and network capabilities, even if the controller is disconnected from the network, the schedule function can be normal operation

- With dual communication interface, containing BACnet and Modbus protocol.

- Site can easily be manually operated with a manual switch.

Technical data

| Control Supply | Output Terminals |
| --- | --- |
| 230V 50/60Hz single phase & neutral at0.1A | Line In, Line Out for each channel 1 x 4mm2 max conductor size |
| Control Inputs | Compliance |
| 2*RS485 BACnet、Modbus | CE OR ROHS |
| User Controls | Operating Environment |
| Service Switch | 0º to 50ºC ambient temperature 0% to 95% RH non condensing |
| Internal Controls | Construction |
| Programmable Logic Controller | ABS DIN rail enclosure |
| Supply Terminals | Dimensions |
| Line, Neutral, Earth 1 x 4mm2 max conductor size | 180（W）*110（D）*77(H) |

Electrical diagram

CH0  IN

CH0 OUT

CH1  IN

CH2  IN

CH3  IN

CH4  IN

CH5  IN

CH1 OUT

CH2 OUT

CH3 OUT

CH4 OUT

CH5 OUT

L

N

L

E

SUPPLY

230V 0.2A

XI0

XI1

XI2

GND

12V

DA+

DA-

A+

B-

mounting dimensions（MM）

BCX-H1020