###### BG-Modbus
BACnet to Modbus Gate

## Features and Highlights

- Interoperable

BACnet-compliant controller supports Modbus data form slave nodes on an EIA-485 or EIA-232 network.  and One MS/TP connections to BACnet internetwork.

- Versatile

Supports 100 analog and  100 binary values integrate Modbus device data with a BACnet system.

- Reliable

Extensive onboard filtering, with all program data backed up in nonvolatile flash memory.

- Ecomomical

Simple, low cost solution for field-level integration of Modbus device.

## Applications and functions

- The Hysine BG-Modbus is a field-level gateway that resides on a BACnet MS/TP network and connects to Modbus over EIA-232 or EIA-485,translating Modbus data to BACnet AVs and BVs. The BG-Modbus appears to the BACnet system in the same manner as a BACview BCU,with a single BACnet device instance.

- The BG-Modbus offers a point capacity of 100 BACnet AVs and 100 BVs an ideal point count for most Modbus applications such as chillers and VFDs. A single BG-Modbus supports up to 10 Modbus devices on a multi-drop Modbus EIA-485 network. A DB-9 connector supports a point-to-point connection to a Modbus device over Modbus EIA-232.

- The BG-Modbus is the next-generation BACnet to Modbus gate from Hysine. Each BG-Modbus supports field controllers on one BACnet MS/TP LANs and one Modbus LANs. MS/TP is a simple twisted-pair bus with a configurable speed to 76.8 Kbps. Modbus LANs is a simple twisted-pair bus with a configurable speed to 9.6 Kbps.

- The BG-Modbus independently executes digital control(DDC) algorithms to orchestrate the operation of field controllers  its MS/TP LANs. It’s programmed at a BACview operator terminal with Hysine’s easy-to-use, Windows-based graphical programming environment , ViewLogic.  Revolutionary features like an extensive application library, drag-and-drop DDC edits, dynamic real-time data updates, and self-documentation save time and ease the setup process.

- The BG-Modbus can access available data as BACnet objects and properties from throughout BACnet internetwork, making its operational status and control data available to other BACnet devices in the same way. This enables an unmatched level of interoperability with other site systems.

- CMOS circuitry,a four layer circuit board with separate ground plane, and extensive hardware software,and power-supply filtering ensure reliable and stable operatio. The CMOS processor uses an internal watchdog,and power supply voltage is monitored to provide automatic shutdown and data backup.

## Ordering information

Item number                             Description                                              .

BG-Modbus                               Modbus and BACnet  MS/TP network

## Technical Data

- Power   24 VAC @ 10VA. Utilizes a half-wave rectifier, which allows a single transformer to power Multiple BRs. One leg of 24VAC connects to earth (panel) ground.

- Battery   Replaceable 3.0V lithium battery provides up to 1.5 years(cumulative) real-time clock(without external power supply). Standby battery life is 10 years. Coin-cell type BR1225 or equivalent.

- Processor & memory    AVR processor with onboard flash memory and RAM.

- BACnet MS/TP   Removable, header-style screw terminal for 1 BACnet MS/TP(shielded  twisted-pair bus)LANs,each individually configurable from76.8 Kbps.

- Modbus Communications  Either EIA-232(serial) to single Modbus device or multi-drop EIA-485 (twisted pair) to up to 10 Modbus device. Network options configurable for ASCⅡ/RTU, 4800 and 9600 baud, even/odd/no parity, and stop bit options for compatibility with various modbus implementations.

- Dimensions    (120mm)H × (140mm)W × (38mm)D

- Environmental   0-55℃.0-95%RH,non-condensing.

- Software   Support for 100 BACnet AVs and 100 BVs, each mapped to a Modbus data point through a string written to the description property of the AV or BV object.

- Ratings   EMC  GB/T 17626

## Dimension[mm]